## Foglio1
16200 | kJ/hr | 4.5 | Kw | UC = | 0.00027778 | Rated Capacity
4.64 | - |  |  |  |  | Rated COP
!An air-water heat pump from Viessman was taken as an example of catalog data (Viessmann, 2020)
!References:
!Viessmann. 2020. “VITOCAL 250-S: Air-to-water heat pump for hybrid operation 1.1 - 13.4 kW” commercial datasheet.
35 | 45 |  |  |  |  | !SUPPLY TEMPERATURE
-7 | -2 | 2 | 7 | 12 |  | !DRY BULB TEMPERATURE
0.25 | 0.5 | 0.75 | 1 |  |  | !PARTIAL LOAD
0.30444 | 0.56897 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = -7 °C and part_load = 0.25
0.45556 | 0.60991 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = -7 °C and part_load = 0.5
0.59333 | 0.62284 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = -7 °C and part_load = 0.75
0.71778 | 0.55603 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = -7 °C and part_load = 1
0.33333 | 0.61853 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = -2 °C and part_load = 0.25
0.5 | 0.66164 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = -2 °C and part_load = 0.5
0.65111 | 0.67672 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = -2 °C and part_load = 0.75
0.80222 | 0.67888 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = -2 °C and part_load = 1
0.35111 | 0.65302 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = 2 °C and part_load = 0.25
0.52667 | 0.69828 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = 2 °C and part_load = 0.5
0.68444 | 0.71336 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = 2 °C and part_load = 0.75
0.84444 | 0.71552 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = 2 °C and part_load = 1
0.48889 | 0.92672 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = 7 °C and part_load = 0.25
0.73333 | 0.99138 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = 7 °C and part_load = 0.5
0.95556 | 1.0129 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = 7 °C and part_load = 0.75
1.1778 | 0.96983 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = 7 °C and part_load = 1
0.52222 | 0.95905 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = 12 °C and part_load = 0.25
0.78222 | 1.0259 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = 12 °C and part_load = 0.5
1.02 | 1.0496 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = 12 °C and part_load = 0.75
1.2556 | 0.97414 |  |  |  |  | !Fraction capacity and COP at T_supply = 35 °C, Dry_bulb = 12 °C and part_load = 1
0.28222 | 0.44181 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = -7 °C and part_load = 0.25
0.42222 | 0.47198 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = -7 °C and part_load = 0.5
0.55111 | 0.48276 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = -7 °C and part_load = 0.75
0.66667 | 0.49569 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = -7 °C and part_load = 1
0.30889 | 0.4806 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = -2 °C and part_load = 0.25
0.46444 | 0.51293 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = -2 °C and part_load = 0.5
0.60444 | 0.52371 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = -2 °C and part_load = 0.75
0.74444 | 0.53664 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = -2 °C and part_load = 1
0.32667 | 0.52802 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = 2 °C and part_load = 0.25
0.48889 | 0.56466 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = 2 °C and part_load = 0.5
0.63556 | 0.57759 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = 2 °C and part_load = 0.75
0.78444 | 0.59267 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = 2 °C and part_load = 1
0.45333 | 0.76724 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = 7 °C and part_load = 0.25
0.68222 | 0.82112 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = 7 °C and part_load = 0.5
0.88667 | 0.76509 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = 7 °C and part_load = 0.75
1.0933 | 0.86207 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = 7 °C and part_load = 1
0.48444 | 0.84483 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = 12 °C and part_load = 0.25
0.72667 | 0.90302 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = 12 °C and part_load = 0.5
0.94667 | 0.84267 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = 12 °C and part_load = 0.75
1.1667 | 0.94828 |  |  |  |  | !Fraction capacity and COP at T_supply = 45 °C, Dry_bulb = 12 °C and part_load = 1
Note on A1: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: declared capacity
Note on A2: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: declared COP